## Slide 1
Slide Rule for Fire Fighting Sprinklers
from Mather & Platt Ltd. / by J. Halden and Co. Ltd. (both UK)
Picture: Anonymous; https://creazilla.com/nodes/25947-fire-clipart; Public Domain License

## Slide 2
What for?
Photo: Brandon Leon / CC BY-SA
Photo: Claudio Losa / Pixabay
Photo: Siggy Nowak / Pixabay
https://sites.google.com/site/historyofmatherplattltd/

## Slide 3
The Slide Rule
≈ 1/2‘‘ / 12mm
≈ 19‘‘ / 48cm

## Slide 4
≈ 1852: Mather & Platt Ltd.
https://sites.google.com/site/historyofmatherplattltd/
Textile Machines
Pumps
Electrical Equipment
Fire Engineering
Chemical Systems
Salford Iron Works (Collin and William Platt)
Mather Textile Machines (William and Collin Mather)

## Slide 5
J. Halden & Co. Ltd.
Drawing Office Materials
Photo Processes
https://www.gracesguide.co.uk/File:Im19071214Loco-Halden.jpg

## Slide 6
Qi
Pressure grade line
h = Δp/(ρ·g)
P
Initial pressure head
Local pressure head
Determine the required discharge (per area and/or per sprinkler) and from this the total discharge
Compute the pressure head loss and therefrom the local pressure head at each sprinkler and the required initial pressure head
Choose adequate type of sprinkler
Qtotal = ΣQi
Sprinkler pipe
3 Steps do design a Sprinkler System
Pressure / Head loss
1
2
3
3
1
2

## Slide 7
Water Demand
Qsprinkler
Asprinkler
1
3
2a
2b

## Slide 8
Friction Head Loss
Initial pressure head
Local pressure head
Diameter (D)
Length (L)
Friction head loss (hf)
Roughness (C)
Discharge (Q)
Hazen-Williams
or
Combined scale
1
3
2a
2b

## Slide 9
An Example
D = 1 inch (steel) (D4.87 ·C1.85)
Q = 17.5 GPM
Δp = 3.8 psi
L = 40 ft
GPM = (US) gallons per minute
1
3
2a
2b
Δp = 3.8 psi
hf = 8.8 ft
1 ft = 0.434 psi

## Slide 10
The Flow Velocity
D = 1 inch
Q = 17.5 GPM
v = 7.4 ft/s
v2 = 55 (ft/s)2
1
3
2a
2b

## Slide 11
Local Head Losses
Луносвет, CC BY-SA-3.0
Fittings
Bends
Valve
Bifurcation
1
3
2a
2b

## Slide 12
Local Head Losses
v2/2g = 0.86 ft
v2 = 55 (ft/s)2
2g = 64.4 ft/s²
L (ft) Δp (psi)
e.g. with x = 1.45 → hL = 1.25 ft or Δp = 0.54 psi
1 inch
Q = 17.5 GPM
Δp = 0.54 psi
1
3
2a
2b

## Slide 13
Equivalent Length for Bends
d
equivalent lenght Le ≈ 20∙d
1
3
2a
2b

## Slide 14
Sprinkler Discharge
Qi
Catalogue Tyco Fire Protection Products, from www.grinnell.com
Photo: Claudio Losa / Pixabay
1
3
2a
2b

## Slide 15
Sprinkler Discharge
Qi
pi = 31.5 psi
Qi = 23 GPM
K = 4.2
1
3
2a
2b

## Slide 16
That‘s It
https://prof.beuth-hochschule.de/heimann/rechenschieber-fuer-das-bauwesen/wasserbau-hydraulic-engineering/?print=1
Here you will find more slide rules for hydraulic engineers
Thank you for your attention
&
thank you Phillip, for providing us this extraordinary slide rule
heimannstefan@yahoo.de